## ### READ ME ###
This calculation tool calculates the probability of Covid-19 infection risk at a site using Wells-Riley and modified Wells-Riley equations. It can be used with citation. Yılmazoğlu M.Z., Covid-19 Infection Risk Calculation Tool, Journal of TTMD, Issue 127, 2020. The web pages in which the tool is available in Gazi University and/or TTMD.
This study prepared by Assoc. Prof. M. Zeki YILMAZOGLU. Dr. M. Zeki YILMAZOGLU Assoc. Prof. Gazi University Faculty of Eng. Dept. of Mechnical Engineering zekiyilmazoglu@gazi.edu.tr
"IMPORTANT NOTE !! This calculation tool cannot give an exact infection risk result due to uncertainties. However, it enables an approach to be made depending on the variables in the location. The ventilation condition of the space, the number of people in the area, the number of infectious sources, the duration of their stay, the amount of infection dose given to the space per hour were stated as variables. The amount of dose given to the room per hour is stated between 3-300 quanta / h for Covid-19 in some literature. In terms of being an average value, the value of 48 quanta / h was preferred in the calculations. It has been left as input so that it can be changed on demand. Selection of the area type under the space parameters is necessary in order to determine the ventilation flow rate. In the case of mechanical ventilation, the ventilation flow rate is calculated according to ASHRAE 62.1 and is also related to the area and height of the space. Therefore, these parameters are also left as variables. Natural ventilation is given as an option, and the hourly air exchange is calculated as 70% of the volume. In addition, if the ventilation flow rate is known or only as small as the leak (if the windows are closed), the user-defined ventilation flow rate option is also given. The filtration status option determines the Wells-Riley model to be used. The 'Yes' option uses the modified Wells-Riley model and the Wells-Riley model with the 'none' option. If the air handling unit in the area is operated continuously, the operating ratio should be 1. Particle capture efficiency varies according to the filter feature. 99.95% value (as 0.9995) can be entered when using HEPA filter. The percentage of probability and the number of possible new cases are shown under the title of results. The calculations were made by considering the respiratory characteristics of the adult individual. The calculations are statistical values ​​only and the high number of sensitive people in the area will affect the result. In addition, if there is a super emitter at the site, it is inevitable that it will affect the results as the amount of dose delivered to the area per unit time will change. Complete mixing of air is stipulated in ventilation. However, this will create some uncertainties in buildings with high floor spacings where complete mixing cannot occur. Within these limitations, this calculation tool reveals an approach with the condition of MASK, PHYSICAL DISTANCE, HYGIENE and shows the importance of ventilation in the prevention of the epidemic. "Although this calculation tool is a simplified tool, it is not recommended for the use of people who are not competent in ventilation to avoid different interpretations. Any direct or indirect accident or wrong design that may be caused by the use of this calculation tool does not hold responsible persons, institutions, and associations authorized to publish this tool.
Ofis
Sınıf/Derslik
Restoran
AVM
Spor Salonu vb.
Yolcu Bekleme
Havaalanı
Var
Yok

## CALCULATOR
Model | Parameters |  |  | Assumed Values |  |  | ASHRAE 62.1
Input | Parameter Name | Unit | Value | Parameter Name | Unit | Value | Occupancy Category | People Outdoor Air Rate | Area Outdoor Air Rate
Probability Percentage | Number of Sensitive Occupants to Infection (S) | person | 30 | Particle Diameter (dpart) | nm | 160 | Office | 2.5 | 0.3
Number of New Cases | Number of Infective Occupants (I) | person | 1 | Average Respiration Rate for an Adult | resp./min. | 16 | Cafeteria/Fast-Food | 3.8 | 0.9
| Exposure Time (t) | h | 0.6 |  | ml/resp. | 500 | Conference/Meeting | 2.5 | 0.3
| Infection Dose Per Hour Emitted to Air (q) | qph/h | 48 | Pulmoner Ventilation Rate (p) | m3/h | 0.48 | Banks or Bank Lobbies | 3.8 | 0.3
[7 empty] | General Manufacturing | 5 | 0.9
| Spatial Parameters |  |  | Results |  |  | Light Assembly | 3.8 | 0.6
| Type | - | Classrooms | Number of New Cases (C) | person | 0.3825 | Courtroom | 2.5 | 0.3
| Area | m2 | 35 | Probability Percentage | % | 1.275 | Barbershop | 3.8 | 0.3
| Height | m | 2.6 |  |  |  | Beauty and Nail Salons | 10 | 0.6
| Filtration | - | Yes |  |  |  | Supermarket | 3.8 | 0.3
| HVAC Operation Fraction (fHVAC) 0 ≤ f ≤ 1 | - | 1 |  |  |  | Classrooms | 5 | 0.6
| Particle Capture Efficiency (ηFilter) | - | 0.75 |  |  |  | Restaurants | 3.8 | 0.9
| Volume | m3 | 91 |  |  |  | Mall Areas | 3.8 | 0.3
| Ventilation Type | - | Mechanical Ventilation |  |  |  | Gym/Sports Area | 10 | 0.3
| Ventilation Flow Rate (User Defined) | m3/h |  |  |  |  | Transportation Waiting | 3.8 | 0.3
| * Ventilation Flow Rate | m3/h | 615.6 |  |  |  | Lounge | 3.8 | 0.3
| ACH | - | 6.7648
* The ventilation flow rate for "Mechanical Ventilation" is calculated according to ASHRAE 62.1.
CALCULATIONS
| According to the Wells Riley Equation |  |  | Accordig to the Modified Wells Riley Equation
| Infection Dose to Air per Unit Time (q) | qph/h |  | Infection Dose to Air per Unit Time (q) | qph/h | 48
| Volumetric Pulmonary Ventilation Rate per Unit Duration of Susceptible Persons (p) | m3/h |  | Volumetric Pulmonary Ventilation Rate per Unit Duration of Susceptible Persons (p) | m3/h | 0.48
|  |  |  | Infectious Particle Captured by Filtration (kfiltr) | 1/h | 5.0736
|  |  |  | Infectious Particle Accumulating on the Surface (kdepos) | 1/h | 1.1043e-06
Office
Classrooms
Restaurants
Cafeteria/Fast-Food
Conference/Meeting
Banks or Bank Lobbies
General Manufacturing
Light Assembly
Courtroom
Barbershop
Beauty and Nail Salons
Supermarket
Mall Areas
Gym/Sports Area
Transportation Waiting
Lounge
Yes
No
Natural Ventilation
Mechanical Ventilation
User Defined

## Case Study
Without ventilation (infiltration flow rate can be considered)
| Exposure time h | Risk Percentage % | Number of new cases
| 0.6 | 31.89 | 9.57
| 1.2 | 53.61 | 16.08
| 1.8 | 68.4 | 20.57
| 2.4 | 78.48 | 23.54
| 3 | 85.34 | 25.6
| 3.6 | 90 | 27
| 4.2 | 93.2 | 27.96
| 4.8 | 95.37 | 28.61
| 5.4 | 96.04 | 29.05
| 6 | 97.85 | 29.36
Natural ventilation
| Exposure time h | Risk Percentage % | Number of new cases
| 0.6 | 2.2 | 0.67
| 1.2 | 4.39 | 1.32
| 1.8 | 6.51 | 1.95
| 2.4 | 8.59 | 2.58
| 3 | 10.62 | 3.19
| 3.6 | 12.61 | 3.78
| 4.2 | 14.45 | 4.36
| 4.8 | 16.44 | 4.93
| 5.4 | 18.3 | 5.49
| 6 | 20.11 | 6.03
Mechanical Ventilation
%75 particle capture effciency + 6ACH | Exposure time h | Risk Percentage % | Number of new cases
| 0.6 | 1.28 | 0.38
| 1.2 | 2.53 | 0.76
| 1.8 | 3.78 | 1.13
| 2.4 | 5 | 1.5
| 3 | 6.21 | 1.86
| 3.6 | 7.41 | 2.22
| 4.2 | 8.59 | 2.58
| 4.8 | 9.76 | 2.93
| 5.4 | 10.91 | 3.27
| 6 | 12.04 | 3.61
Area 35 m2, height 2,6 m without ventilation number of people 30